## Slide 1: Francis turbines

## Slide 3
2. Different Parts:
    Penstock:
    It is a large sized conduct which conveys water from the upstream of the dam / reservoir to the T runner.
    Spiral / scroll casing:
    It constitutes a closed passage whose X-section area gradually decreases along the flow direction, area is maximum at inlet and nearly zero at exit.

## Slide 4
2. Different Parts:
    Guide vanes / wicket gates:
    These vanes direct the water into the runner at an angle appropriate to design. It is operate by hand wheel or automatically.
    Governing mechanism:
    It changes the position of GV to affect the variation in water flow rate, when the load conditions on the T change.

## Slide 5
2. Different Parts:
    Runner and runner blades:
    The driving force in the runner is both impulse and reaction.
    Runner blade no. = 16 ~ 24.
    Draft tube:
    It is gradually expanding tube which helps easy discharges water, passing through runner to the tail race. Thus it helps to reuse of the exit water.

## Slide 6: Parts of A Francis Turbine

## Slide 7
Runner inlet (Φ 0.870m)
Guide vane outlet for designα) (Φ 0.913m)
Closed
Position
Max. Opening Position

## Slide 8: Operation of Guide Vanes
.

## Slide 9
Water from spiral casing
Water particle

## Slide 10: Parts of A Francis Turbine

## Slide 11
Outlet
draft tube
Outlet
runner
Inlet
runner
Inlet
guide vane
Outlet
guide vane
hatm
Ideal Hydraulic Energy Diagram

## Slide 12
Hydraulic efficiency of Francis Hydraulic System

## Slide 13
Gap losses
Friction losses in
the spiral casing
and stay vanes
Guide vane losses
Friction losses
Runner losses
Draft tube losses

## Slide 14: Losses in Francis Turbines
Draft tube
Output Energy
Head [m]
Hydraulic Efficiency [%]

## Slide 15
Losses in Francis Turbines
Hydraulic Efficiency [%]
Output Energy
Output [%]

## Slide 16: Spiral Casing
Spiral Casing : The fluid enters from the penstock to a spiral casing which completely surrounds the runner.
This casing is known as scroll casing or volute.
The cross-sectional area of this casing decreases uniformly along the circumference to keep the fluid velocity constant in magnitude along its path towards the stay vane/guide vane.

## Slide 18
3. Construction (different Parts):

## Slide 19
3. Construction (different Parts):

## Slide 25
3. Construction (different Parts):

## Slide 26
3. Construction (different Parts):

## Slide 27
4. Working:
    Water under pressure (from reservoir and penstock) enters the runner from the G/Vs towards the center in radial direction and discharges out of the runner axially.
    Energy of water transfer to rotational energy of runner then rotation of shaft.
    There is a difference of pressure between the G/Vs and the runner which is called reaction pressure and is responsible for the motion of the runner.

## Slide 28
4. Working:
    The pressure at inlet is more than outlet.
    Water flow through the spiral casing.
    Water release from a draft tube submersed in water for easy release and reuse of exit water.

## Slide 29: Calculation ( v ):
Work done = Q (Vw1u1  Vw2u2)
Work done = maximum when Vw2=0 for the given conditions.
H= Q (Vw1u1  Vw2u2) / gHQ
= 85~90

## Slide 30: Mechanical
M= power available at T shaft / power developed by the T runner
= shaft power / bucket power (power develop by runner)
= P / [Q (Vw1u1  Vw2u2)]
It is due to bearing friction etc.

## Slide 31: Over all
O= [power available at the turbine shaft] / [power available from the water jet]
= shaft power / water power
= P / gHQ
O= H M
= 80~90
[V= Qa /Q = 100]
6.Hydraulic electric plant efficiency-6:
HE = G O
HE = Pout of HE / gHQ

## Slide 32: Design of Francis Turbine

## Slide 33
Velocity triangles
rri
rre
Uri
Vwi
Vri
Vfi
Vai
Ure
Vwe
Vre
Vfe
Vae
bi
ai
be
ae

## Slide 34
Inlet Velocity Triangles Vs Ns
Low Specific Speed : Slow Francis Runner
Vwi
Vai
Vfi

## Slide 35
Inlet Velocity Triangles Vs Ns
Low Specific Speed : Normal Francis Runner
Vwi
Vai
Vfi

## Slide 36
Inlet Velocity Triangles Vs Ns
High Specific Speed : Fast Francis Runner
Vwi
Vai
Vfi

## Slide 37: Specifications of Runner
Slow Runner: Ns=60 to 120
  ai = 150 to 250
  Kui = 0.62 to 0.68
  bi = 900 to 1200
  B0/Dp=0.04 – 0.033
Normal Runner: Ns = 120 – 180
  ai = 120 to 32.50
  Kui = 0.68 to 0.72
  bi = 900
  B0/Dp=0.125 to 0.25
Fast Runner: Ns = 180 to 300
  ai = 32.50 to 37.50
  Kui = 0.72 to 0.76
  bi = 600 to 900
  B0/Dp=0.25to 0.5

## Slide 38: Selection of Exit Velocity Triangle
Exploitation of Reaction Character…..

## Slide 39: Energy of Water Leaving a Francis Runner
RE
TE
Zre
Zte
Vte
Vare
HTW

## Slide 40
Hydraulic Energy of Exiting Fluid
For frictionless flow through exit tube
For frictional flow through exit tube
For maximum energy recovery

## Slide 42: Components of Draft Tube

## Slide 43: Geometric Ratios for Draft Tube

## Slide 44
NPSH required

## Slide 45
Dimensions of the outlet
13o < be < 22o
1,05 < a < 1,15
0,05 < b < 0,15
Highest value for highest head

## Slide 46: Internal Anatomy of Runner

## Slide 47: Blade Velocity Vs Tangential Component of Fluid Velocity
Ub
Ub
Vw
Va
Vf
Vr
In maridional plane at mean radius of rotor

## Slide 48: Runner Design

## Slide 49: Runner Design
The main procedure in design of a new runner includes;
Use of Classical theory for shaping the blade geometry
CFD analysis for the tuning of runner geometry
The classical method;
Design the meridional plan of runner based on available methods
Obtain the perpendicular view of runner using conformal Mapping.
Modify using model testing or CFD.

## Slide 50: Runner Design

## Slide 51: Shape of Francis Channel : Meridional Plan
Rr1i
Rr2e
L/Dri
Rr2i
Rr1e

## Slide 52: Real values of Radii
The real value of the outlet tip radius
The real value of the intlet root radius
Rr2e and Rr1i are only fix two points of the leading and trailing edges and the rest of these curves should be drawn to lead to better efficiency of runner.

## Slide 53: Determination of Inlet & exit edges runner
1i
2i
1e
2e
The form of these edges is two parabolic curves.
Define the non-dimensional specific speed
For
the leading edge form is a parabolic arc
with the peak in the point by radius of 2.Rr1i-Rr2iwhich passes through the points 1i and 2i,