## Slide 1: Centrifugal Pump
Rudra Ghimire

## Slide 2: Centrifugal Pump
Centrifugal Pump can be defined as a mechanical device used to transfer liquid of various types.
As the name suggests, it relies on the principal of Centrifugal force.
It converts the energy provided by a prime mover, such as an electric motor, steam turbine, or gasoline engine, to energy within the liquid being pumped.

## Slide 3
1- Casing:-
This is named from the spiral shape of the casing which is so constructed to act as a collector for the liquid as it leaves the outer edge of the impeller vanes. In volute pumps area of flow gradually increases from throat towards the delivery pipe. The increase in area of flow decreases the exit velocity and hence pressure increases in the casing.
Volute
Suction
Impeller
Construction of Centrifugal Pumps
Casing generally are three types:
I. Volute casings for a higher head.
6

## Slide 4: Construction of Centrifugal Pumps
II. Vortex casing
Vortex casing is a casing in which circular chamber is provided between the casing and the impeller. Vortex casing will increase pump efficiency by reducing eddies formation to a considerable extent.
III. Circular casigs
In diffuser casing, the fluid passes through a ring of fixed vanes or diffuser after the fluid has left the impeller, that diffuse the liquid, this provides a more controlled flow and a more efficient conversion of velocity head into pressure head. Providing fixed diffuser increases the efficiency of the pump up to 90 percent.

## Slide 5: Rotating component
It consists of shaft and impeller. Shaft is coupled with a motor to give drive to the pump. An impeller is a rotating component of a centrifugal pump, usually made of iron, steel, bronze, brass or aluminium which transfers energy from the motor that drives the pump to the fluid being pumped by accelerating the fluid outwards from the center of rotation.

## Slide 6: Different types of impeller
Open type impeller:
It consists of vane which accelerates the fluid. The number of vanes can vary from 2 to 8 or more.
Semi-closed impeller:
It consists of vane attached to plate on one side. Industrial application of such types of impeller is for pumping liquids containing suspensions.
Closed impeller:
The vane is enclosed by two disc or plates. Shrouds or sidewall encloses the vanes. The liquid moves in between the cavity between the vanes and plates.

## Slide 7
Radial flow
Axial flow
Mixed flow
2-Impeller
Three main categories of centrifugal pumps exist
7

## Slide 8: Centrifugal Impellers
Diameter of
the Impeller
Thickness
of the impeller
Thicker the Impeller- More Water
Larger the DIAMETER - More Pressure
Increase the Speed - More Water and Pressure
Impeller
Vanes
“Eye of the Impeller”
Water Entrance

## Slide 9: Two Impellers in Series
Direction of Flow
Twice the pressure
Same amount of water

## Slide 10: Multiple Impellers in Series
Placing impellers in series increases the amount of head produced
The head produced = # of impellers x head of one impeller
Direction of Flow
Direction of Flow

## Slide 11: Operating Principals
As mentioned earlier, Centrifugal pump relies on the centrifugal force.
When you swing a bucket of water around over your head, you will find that as you increase the speed, the bucket is pulled harder against your arm. This pull on your arm is the centrifugal force. It makes no difference if you swing the bucket horizontal or vertical. If the speed is fast enough, then the water will remain on the bucket.

## Slide 12: Operation Principals continued.….
If you punch a small hole on the bottom of
bucket, the water throws a stream and the distance the water travels is proportional to the centrifugal force.
The same force that kept water in the bucket, is how the simple Centrifugal pump works.

## Slide 13: Operation Principals continued.….
Centrifugal Pump consists of a rotating impeller inside a stationary volute (casing).
Liquid enters the pump through the suction inlet into the eye of the impeller.
The speed of the rotating impeller then forces the liquid out through the discharge nozzle.

## Slide 14: Operation Principals continued…..
The liquid enters the inlet of the centrifugal pump under atmospheric pressure, and flows into the eye of the impeller.
The Centrifugal force exerted on the liquid by the rotating impeller, moves the liquid away from
the impeller eye and out along the impeller vanes to their extreme tip where the liquid is then forced against the inside walls of the volute
and out through the discharge of the pump.
Due to the reduction of pressure occurring
at pump inlet and impeller eye, liquid is drawn
into the pump in continuous flow as it moves
through the pump.

## Slide 15
The shape of the volute casing is such that it is wider at the discharge point than where the liquid is first forced by the impeller against the volute.
When the water from the impeller strikes the side of the volute, the velocity is increased. This accelerated motion is called “Kinetic Energy”, which is the energy in motion.
The shape of the volute permits the liquid to expand, which slows down the motion of the liquid. As soon as the liquid slows down inside the volute, Kinetic Energy is transformed into pressure. This pressure
then forces the liquid out of the pump discharge nozzle into the outlet pipe lines.
Operation Principals continued…..

## Slide 16
C/P connected with SP and DP

## Slide 17: pump heads
Static Suction Head (hs):
It is the vertical distance between the centre of the impeller to the free surface of the water from where water is to be pumped. If the liquid level is above pump centerline, hs is positive. If the liquid level is below pump centerline, hs is negative. Negative hs condition is commonly denoted as a suction lift.
Static Discharge Head (hd):
It is the vertical distance between the pump centerline and the point of free discharge or the surface of the liquid in the discharge tank.
Total Suction Head (hs):
It is the suction reservoir pressure head (hps) plus the static suction head (hs) plus the velocity head at the pump suction flange (hvs) minus the friction head in the suction line (hfs).
HS = hps + hs + hvs + hfs
Total Discharge Head (hd):
It is the sum total of discharge reservoir pressure head (hpd), static discharge head (hd), the velocity head at the pump discharge flange (hvd) and the total friction head in the discharge line (hfd).
hd = hpd + hd + hvd + hfd

## Slide 18: Manometric head

## Slide 19
When a pump is filled with the fluid to be operated at normal speed with discharge closed, the head developed is called SH.
The force vortex create with pressure head difference between eye and impeller periphery is (u22 –u12)/2g.
There is great deal of circulation within the impeller which cause rotation of fluid in all parts of impeller , eye and several distance of intake pipe. So actual shutoff head is approximately u22 / 2g.
Shutoff head depends on impeller vane  at inlet and exit and nature of intake.
Shut off Head of pumps:

## Slide 20: Pump head
The head that the pump must develop
= static lift + total head loss

## Slide 21
Heads of Pump:
where :
Vs = Velocity of fluid in the suction pipe.
Vd = Velocity of fluid in the delivery pipe.
hs = Suction head.
hd = Delivery head.
hfs = head losses in the suction pipe.
hfd = head losses in the delivery pipe.
10
Static head (Hst)
Hst = hs + hd

## Slide 22
Manometric head (Hm) :
but
and
where hf = hfs + hfd
(where HL = impeller losses)
Total head (H)
(where )
When Vs = Vd
Hence Hm = H
11

## Slide 23
There are three main categories of impeller due type of impeller’s vane, which are used in the centrifugal pumps as;
Radial vanes, Fig. (a).
Backward vanes, Fig. (b).
Forward vanes, Fig. (c).
12
Type of Impeller

## Slide 24
a) when β2 > 90o, the Forwards curved vanes of the impeller.
b) when β2 = 90o , the radial curved vanes of the impeller.
c) when β2 < 90o, the Backwards curved vanes of the impeller.
where :
V = absolute velocity of the water.
U = Tangential velocity of impeller (peripheral velocity).
Vr = relative velocity of water to the wheel.
Vf = velocity flow.
N = Speed of impeller in (rpm).
13

## Slide 25: Pump Performance Curve Mapping the Flow and the Head
Pump Flow Rate
Most pump performance curves slope from left to right
Performance Curve
Head

## Slide 26: Pump Performance Curve Important Points
Shut-off Head is the maximum pressure or head the pump can produce
No flow is produced
Pump Flow Rate
Head
Shut-off Head

## Slide 27: Pump Performance Curve Important Points
Pump Flow Rate
Head
Maximum Flow
Maximum Flow is the largest flow the pump can produce
No Head is produced

## Slide 28
The friction loss is mapped onto the graph
The amount of friction loss varies with flow through the system
Head
Pump Flow Rate
Friction Loss
System Performance Curve
System Performance Curve is a mapping of the head required to produce flow in a given system
A system includes all the pipe, fittings and devices the fluid must flow through, and represents the friction loss the fluid experiences

## Slide 29
Head
Pump Flow Rate
The point on the system curve that intersects the pump curve is known as the operating point.

## Slide 30: Pump Performance Curve
The main characteristic curves of a centrifugal pump consists of variation of head (hm), power (P) and discharge (Q) with respect to speed

## Slide 31: Pump Performance Curve
The operating characteristic curves is shown in fig

## Slide 32
Theoretical Head Developed by an Impeller
Leakage and Recirculation Losses
Theoretical head (Euler head)
Leakage/Recirculation losses
Flow rate, Q
Head, H

## Slide 33
Hydraulic Losses
Pumps are designed trying to achieve a no pre-rotation condition close to the best efficiency point, since this condition minimize shock-losses. In other words, shock losses increase as we move away from the BEP.
Theoretical Head Developed by an Impeller

## Slide 34
Hydraulic Losses
Other losses including friction, mixing, change in direction of fluid, separation, etc. also contribute significantly to the total losses due to hydraulic.
Theoretical Head Developed by an Impeller
Theoretical head (Euler head)
Hydraulic losses
Flow rate, Q
Head, H

## Slide 35
Friction Losses
Friction losses increases with increasing flowrate and viscosity.
Theoretical Head Developed by an Impeller
Theoretical head (Euler head)
Friction losses
Flow rate, Q
Head, H

## Slide 36
Mechanical Losses
These losses include disk friction and frictional losses in bearings. The most significant loss is the thrust bearing loss. The mechanical losses do not have any effect on head and capacity of a pump but increase the brake hoursepower.
Theoretical Head Developed by an Impeller

## Slide 37
Total Losses
Theoretical Head Developed by an Impeller
Theoretical head (Euler head)
Flow rate, Q
Head, H
Leakage/Recirculation losses
Hydraulic losses
Friction losses
Actual Head

## Slide 38
The hydraulic horsepower is the energy transmitted to the fluids by the pump.
The break horsepower is the energy required by the pump shaft to turn. Some of this energy is dissipated inside the pump.
The ratio between the hydraulic horsepower and the break horsepower is the pump hydraulic efficiency.
Theoretical Head Developed by an Impeller
Horsepower

## Slide 39
In practice, a pump is tested by running it at a constant speed and varying the flow by controlling the choke. During the test, Q, DP, and the break horsepower are measure at several points. The DP is then converted to head and the overal efficiency of the pump is calculated. Based on these data, we can develop the pump performance.
The performance curve of a centrifugal pump can be summarized in only one curve of head vs. flowrate for all low viscous fluids.
Theoretical Head Developed by an Impeller
Pump Performance

## Slide 40
Theoretical Head Developed by an Impeller
Pump Performance

## Slide 41: Pump Efficiency
Pump efficiency, η (%) is a measure of the efficiency with which the pump uses the input power to convert the energy into useful output.
η = Pout/Pin
where
η = efficiency (%)
Pin = power input
Pout = power output

## Slide 42
Pump Efficiencies
1- Hydraulic Efficiency (ζh)
The normal value varies between 60% - 90%
2- Manometric Efficiency(ζm)
3 -Volumetric Efficiency (ζv)
The normal value lies between 97% to 98%
14

## Slide 43
4- Mechanical Efficiency (ζ)
It is due to losses in the shaft, coupling, and other operation losses as vibration
The normal value is 95% - 98%
5 - Overall Efficiency (ζo)
The normal value is 71% - 86%
15

## Slide 44
6- Power Required to Drive a Centrifugal Pump
(hp)
(hp)
7 -1 Cavitation
Cavitation is defined as the phenomenon of formation of vapor bubbles of flowing liquid in a region where the pressure of the liquid falls below its vapor pressure and the sudden collapsing of this vapor bubbles in a region of higher pressure. When the vapor bubbles collapse, a very high pressure is created. The formation and the collapse of a great number of bubbles on the surface produce intense local stresses that damage the surface by fatigue. It may occur at the entry to pumps or at the exit from hydraulic turbines in the vicinity of the moving blades
16
The cavitation phenomenon develops in the impeller pump, when the pressure of liquid falls below the saturated vapor pressure at the prevailing temperature ( Ps< Pv of liquid), small vapor bubbles begin to form and the dissolved gases are evolved. The vapor bubbles are caught up by the following liquid and swept into a region of higher pressure, where they condense. Condensation takes place violently, accompanied by a tremendous increase in pressure, which has the character of water hammer blows. These impact follow each other in rapid succession, the vapor bubbles bursting both in the immediate vicinity of the surface attacked and in the pores causing cavitation pitting with many effecting.
7 -2 Cavitation processes in centrifugal pump

## Slide 45
Specific speed of a pump is defined as the speed of a geometrically similar pump which delivers unit discharge under unit head.
Ns = N√ Q / H3/4 --------------------------(10.4)
Specified Speed

## Slide 46
  Pumps are selected in the basis of their essential data:
  No. of units required
  Nature of liquid to be pumped
  Capacity
  Suction condition
  Discharge condition
  Total head
  Service
  Power
  Space, weight, transportation
  Location of installation
  Others: special requirements as design, construction and performances.
Selection of pumps:

## Slide 47
A centrifugal pump delivers water at the rate of 1800 lpm,to a height of 20m, Through a 0.1m, dia, 80m. long pipe. Find the power required to drive the pump, if the overall efficiency is 65%, and Darcy’s friction factor=0.02.

## Slide 49
The following data refer to a centrifugal pump static head = 40m, suction height 5m, dia of suction and delivery pipes = 0.1m, loss of head in suction pipe = 2m, loss of head in delivery pipe = 8m, impeller dia at outlet =0.4m, impeller breadth at outlet 25mm.blades occupy 10% of the outlet area, speed 1200rpm. Exit angle of blade = 1500 with the tangent, Manometric efficiency = 80%, overall efficiency = 70%. Find the power required to drive the pump and what pressures will be indicated by the gauges mounted on the suction and delivery sides.

## Slide 50: Net Positive Suction Head (NPSH)
  NPSHA is the theoretical amount of head that could be lost between suction and point of minimum pressure without causing cavitation (but this always overestimates actual amount that can be lost, because some velocity head must remain, even at point of pmin).
  Net Positive Suction Head Available (NPSHA): The absolute dynamic head at the pump inlet (suction) in excess of the vapor pressure

## Slide 51: NPSH and Cavitation
  Net Positive Suction Head Required (NPSHR): The minimum value of NPSHA that is needed to prevent cavitation in the pump, i.e., the value of NPSHA that causes pmin to equal pvap.
  NPSHR is determined experimentally by pump manufacturers and reported as a function of pump flow rate (usually called ‘capacity’).
  To avoid cavitation, always operate with NPSHA ≥ NPSHR.

## Slide 55
Deep well Turbine Pump:
2 or more impellers are arranged in series and vertical shaft
Q is same: H = nH
Small dia of well casing 
    small dia of impeller 
    H developed in one stage is small  need no. of stages
  Casing not concentric but volute 
    Water discharge to from one impeller to eye of other and need Diffuser vanes

## Slide 56
ns= [neQ] / h3/4
Specific speed of pumps:

## Slide 57
Operating point

## Slide 58
Assume: steady flow
Neglect viscous work and heat transfer
Velocity in inlet and outlet are uniform
Incompressible flow
Applying Bernoulli head,
H=(p/rg + v2/2g +z)2 - (p/rg + v2/2g +z)1 = hs - hf------------------------------(1.1)
H = Head output generated by pump
hs = Head supplied
hf = Head loss
v1 = v2, and z1 = z2, usually
H=(p2+p1)/rg
Basic output parameters:

## Slide 59
H vs Q curve may be transfer into for some other N by similarity laws (Q  n and h  n2) but  dec as it moves away from optimum N.
 dec. if pump is not operation at optimum pt. and dec depends upon how far the mode of opt.

## Slide 61
  Flat char. shows variation in Q with little variation in H
  Steep char. shows variation in H with little variation in Q
  Axial/P has much steeper H-Q curve than Cent/P

## Slide 62
  Flat char. shows variation in Q with little variation in H
  Steep char. shows variation in H with little variation in Q
  Axial/P has much steeper H-Q curve than Cent/P
  A/P  Break/P in high at shutoff but low even after max
  ( so not good and starting and cont operation at low capacity)
  It is fixed blade type but can made adjustable blade as K/T to suit at low and other Q.
  H-Q curve:

## Slide 63
Hydraulic loss:
      Shock Loss: due to turbulence due to improper relative-velocity  at vane inlet. It is large at (low and high) Q small at opt. cond.
      Fluid friction Loss: due to passage between vanes. It varies as Q2.
      Circulatory loss at exist: due to difference in pressure on two sides of each vane. Almost constant wit respect to Q.
Mechanical Loss: due to bearing, packing and disk friction.
Leakage Loss
Power transmitted to impeller
Energy losses in pumps:

## Slide 65
  Minimize this factor for satisfactory operation of pump( good  and prevention of impeller damage).
  Cavitation Increase is indicated by drastic change in .
  It depends on operating condition and design of the pump.
  It changes as change in H and Q.
Cavitation in pumps:

## Slide 66
Effect of Viscosity in pumps:

## Slide 67
  As Viscosity increases H-C curve become more steeper and power required increases.
  The dash line indicates the max  for each V curve.
  H and Q at point of max. V decreases as increase in V because of large increase in Break power.
  If opt =0.85 for water then opt =0.47 when pumping a liquid of viscosity 116 times or centistoke.
Effect of Viscosity in pumps:

## Slide 68
Efficiency of pumps:
  opt for morden large pumps with runner profile and gradual merginig from one type to other.
   decreases as pump size decreases.

## Slide 69
  The discharge = outlet area  av. Velocity
  The effective area for radial(a) and mixed(b) flow impeller = fDB
  for axial(c) impeller = fDe2/4
Calculation of Q and A for pumps:

## Slide 71
  Pumps are selected in the basis of their essential data:
  No. of units required
  Nature of liquid to be pumped
  Capacity
  Suction condition
  Discharge condition
  Total head
  Service
  Power
  Space, weight, transportation
  Location of installation
  Others: special requirements as design, construction and performances.
Selection of pumps:

## Slide 72
  Chose pump under normal condn of operation near to OP. If not loss of energy and uneconomic.
  Criteria for chose of pump: design, sp speed, size, types
  When pumps are connected in combination (series and parallel) need similar H-Q curve through out the range of operation.
      One pump carry most of the load and under certain condition all of the load , with other pump as hindrance rather than help.
      In parallel condition of back flow may occor.
  Need to check cavitation problem.
  Do by plotting pum charasteristic and pipe system charasteristic curve.
  Select by changing speed or size. Speed change reduce .
System characteristics for pumps:

## Slide 74: Advantages and Disadvantages of Centrifugal Pumps
Centrifugal Pumps are the most widely used type of pump for the transfer of liquids. There are many advantages and disadvantages associated with Centrifugal Pumps:
Advantages:
  Simple operation.
  Low first cost and maintenance.
  Insignificant excessive pressure build up in casing.
  Impeller and shaft are the only moving parts.
  Quiet operations.
  Wide range of pressure, flow and capacities.
  Utilize small floor space in different positions.

## Slide 75: Advantages and Disadvantages of Centrifugal Pumps Continued…..
Disadvantages:
  High viscous liquids are not handled well.
  Centrifugal Pumps usually don’t have the capabilities of handling high pressure applications in comparison to other types of pumps, i.e., Regenerative turbines.
  In general, Centrifugal pumps cannot deliver high pressure without changes in design and are not suitable for high pressure delivery at low volumes except the multistage pumps.

## Slide 76: Thank You.